Product Specifications

B 1 T Basket strainer

- General:

  - “Basket” Pipeline strainers shall be installed where shown on plans or required by equipment manufacturers.

  - Strainer shall remove debris from the pipeline to prevent damage to other equipment.  When possible, screen opening size shall be coordinated with the other equipment manufacturers.

- Product:

  - Basket Strainer shall be model “B-1-T" as manufactured by The Metraflex Company®, Chicago, IL.

  - Materials:

    - Strainer body shall be ASTM A126 B Cast Iron.

    - Screens shall be Type 304 Stainless steel.

  - Flanges shall be 125 lb. cast iron in accordance with ASME B16.5

  - Pressure ratings shall be:

    - For liquid service for 2” through 12” rated for 175 PSI at 150⁰ F.

    - For steam service for 2” through 12” rated for 125 PSI at 350⁰ F.

  - Unless specified otherwise, screen perforations shall be:

    - For liquid service for sizes 2” – 3” perforation shall be .045”.

    - For liquid service for sizes 4” – 12” perforation shall be .125”.

    - For steam service for sizes 2” – 3” perforation shall be .045”.

    - For steam service for sizes 4” – 12” perforation shall be .125”.

  - Basket strainer shall be equipped with drain.

- Execution:

  - Basket Strainer shall be installed in accordance with manufacturer’s recommendations and contact requirements.

  - Pressure drop values shall comply with Fluid Controls Institute Standard for performance testing strainers for liquid service.

  - Screen perforation shall be in accordance with equipment manufacturer’s recommendations.