Product Specifications

Note to users: items shown in red indicated edits / selections that need to be made to tailor the specification for the application.

Retain and edit "Delegated-Design Submittal" Paragraph 1.h below if design services have been delegated to the contractor.  The delegated design may be completed entirely by the contractor or may also involve the equipment manufacturer.  Typically, the contractor would be responsible for the means and methods to attach anchors and guides to the structure, and field-fabrication of anchors.  Expansion joint manufacturers may be involved in the piping analysis and selection of expansion joints and placement of anchors and guides.

Hoses Listed for Gas Service with carbon steel or stainless-steel fittings.

- General

  - Provide flexible hose (s) as indicated on the contract drawings or as required to accommodate any thermal expansion, contraction, or vibration.

  - Flexible hose shall be manufactured complete with a section of corrugated metal house, compatible braid, with inlet and outlet connections.

  - Flexible hose shall impart no thrust loads to system support, anchors or building structure.

  - Flexible hose (s) for flammable liquid or gas service up to 4” shall be CSA / AGA listed and be in conformance with UL-536.

  - All flexible hose (s) shall be manufactured in accordance with the documented manufacturers weld procedure specifications in accordance with ASME Section IX.

  - All flexible (s) shall be manufactured in accordance with ASME / ANSI B31.1

  - Delegated-Design Submittal: Provide analysis signed and sealed by a qualified professional engineer.  Submittal shall include [edit as required for project]:

    - Design Calculations: Calculate requirements for thermal expansion of piping systems and criteria for selecting and designing expansion joints, hard-pipe loops, and swing connections.

    - Schedule and drawings: Indicate type, manufacturer's number, size, material, pressure rating, end connections, and locations for each expansion joint, anchor and guide.

    - Anchor Details: Detail fabrication of each anchor indicated. Show dimensions, methods of assembly, and attachment to building structure.

    - Alignment Guide Details: Detail field assembly and attachment to building structure.

- Products

  - Flexible hose to be "Gas Hose®” as manufactured by The Metraflex Company®, Chicago, IL.

  - Corrugated Hose Stainless Steel Type 321 in accordance with ASTM A240

  - Braid shall be 304 Stainless Steel in accordance with ASTM A240.

  - End fitting materials of construction.

    - Stainless steel shall Sch 40 S Type 304 in accordance with ASTM A240

    - Carbon steel standard weight ASTM A54b ERW

  - End fittings shall match fitting material.

    - Weld end in accordance with ASME B16.9

    - MPT in accordance with ASME B1.20.1

    - Raised Face Slip on Flange in accordance with B16.5.

- Execution

  - Install and guide per manufacturers’ installation instructions and Mechanical Contractors Association of America “Guidelines for Quality Piping Installations”.

  - Flexible hose expansion loop return fitting shall be supported to allow movement.