Product Specifications

Insulated Spider Type Pipe Guides.

- General

  - Provide insulated pipe guides as indicated on project plans or in accordance with EJMA guidelines based on design pressure and line size.

  - Primary and intermediate guides shall be pre-insulated spider type.

- Products

  - Pipe guides shall be style “PG Insulated Pipe Guide” as manufactured by The Metraflex Company®, Chicago, IL.

  - All components shall be manufactured in compliance with the Manufacturer's Standardization Society (MSS) SP-58 and SP-89

  - Guide shall be made up of a guide cylinder with bolt down base and a two-section guide spider with 1/8” clearance and insulation.

  - Insulation shall be Johns Manville T-1200 Calcium Silicate insulation.

    - Insulation shall have 450 PSI compressive strength per ASTM C656, Type II, Grade 5

    - Insulation shall have a K-Factor: .62 @400⁰ F in accordance to ASTM C-518

    - Insulation shall have a Flame Spread -0-, Smoke developed -0-. In accordance with ASTM E-84

  - Guide shall be made up of ASTM A-134 carbon steel.

  - Insulated Guide cylinder shall be sized to accommodate pipe insulation.

  - Guide spider shall be sized to accommodate thermal movement.

  - All surfaces of guide shall be coated with fusion bonded powder coating.

- Execution

  - Install per manufacturer’s installation instructions and Mechanical Contractors Association of America “Guidelines for Quality Piping Installations”.

  - Spider type guides are rated to restrain lateral loads only and do not replace pipe supports.