Product Specifications

Specifications for LPD Mighty Mag “Y” Strainer with Magnet

- General:

  - “Y” Pattern pipeline strainers shall be installed where shown on plans or required by equipment manufacturers.

  - Y Strainer shall be of the high-performance low pressure drop design.

- Product:

  - Y Strainer shall be model “LPD-Mighty-Mag" as manufactured by The Metraflex Company®, Chicago, IL.

  - Strainer body shall be ASTM A240 Type 304 Stainless Steel.

  - LPD-Mag should be equipped with minimum 8000 Gauss magnet(s)

  - Type 304 Stainless steel magnet tube shall be installed in a Type 304 stainless steel drywell

  - Screens shall be Type 304 Stainless steel.

  - Screen perforations shall be 20 mesh

  - Strainer shall have a screen pitch of 28.5°

  - Screens shall be removable via a access cover sealed with EPDM O-ring.

  - Strainer shall be equipped with a dry well port.

  - Strainer connection shall be FPT.

- Execution:

  - Y Strainer shall be installed in accordance with manufacturer’s recommendations and contact requirements.

  - Pressure drop values shall comply with Fluid Controls Institute Standard for performance testing strainers for liquid service.

  - Screen perforation shall be in accordance with equipment manufacturer’s