Product Specifications

M 2 K N 250 lb. Y Strainer

- General:

  - “Y” Pattern cast iron flanged pipeline strainers shall be installed where shown on plans or required by equipment manufacturers.

  - Strainer shall remove debris from the pipeline to prevent damage to other equipment.  When possible, screen opening size shall be coordinated with the other equipment manufacturers.

- Product:

  - Y Strainer shall be model “M 2 K N" as manufactured by The Metraflex Company®, Chicago, IL.

  - Materials:

    - Strainer body shall be ASTM A126 B Cast Iron.

    - Screens shall be Type 304 Stainless steel.

  - Flanges shall be 250 lb. class cast iron in accordance with ASME B16.5.

  - Screen perforations shall be:

    - For liquid service for sizes 2” – 4” perforation shall be .062”.

    - For liquid service for sizes 5” – 12” perforation shall be .125”.

    - For steam service for sizes 2” – 10” perforation shall be .045”.

    - For steam service for 12” perforation shall be .125”.

  - Pressure ratings shall be:

    - For liquid service for sizes 2” – 12” rated for 500 PSI at 100⁰ F.

    - For steam service for sizes 2” – 12” rated for 250 lb. at 450⁰ F

- Execution:

  - Y Strainer shall be installed in accordance with manufacturer’s recommendations and contact requirements.

  - Pressure drop values shall comply with Fluid Controls Institute Standard for performance testing strainers for liquid service.

  - Screen perforation shall be in accordance with equipment manufacturer’s recommendations.