Product Specifications

Specifications for LPD High Performance “Y” Strainer

- General:

  - “Y” Pattern pipeline strainers shall be installed where shown on plans or required by equipment manufacturers.

  - Y Strainer shall be of the high-performance low pressure drop design with the following minimum CV values.

2” Pipe	120

2 ½” Pipe	160

3” Pipe	227

4” Pipe	457

5” Pipe	600

6” Pipe	976

8” Pipe	1,607

10” Pipe	2,574

12” Pipe 	3,200

- Product:

  - Y Strainer shall be model “LPD" as manufactured by The Metraflex Company®, Chicago, IL.

  - Strainer body shall be ASTM A126-B Cast Iron.

  - Screens shall be Type 304 Stainless steel.

  - Screen perforations shall be;

    - For liquid service for sizes 2” – 3” perforation shall be .045”

    - For liquid service for sizes 4” – 12” perforation shall be .125”

    - For steam service for sizes 2” – 6” perforation shall be .045”

    - For steam service for sizes 8” – 12” perforation shall be .062”

  - Strainer shall have a screen pitch of 22.5°

  - Screens shall be removable via a access cover sealed with O-ring.

  - Strainer shall be manufactured with .25” pressure differential ports, with one placed on each side of the screen.

  - Strainer shall be equipped with a dry well port.  Port shall be .5”   for sizes 2” – 3” and 1” for sizes 4” – 12”.

  - Strainer connection shall be 125 lb. class flange.

- Execution:

  - Y Strainer shall be installed in accordance to manufacturer’s recommendations and contact requirements.

  - Pressure drop values shall comply with Fluid Controls Institute Standard for performance testing strainers for liquid service.

  - Screen perforation shall be in accordance with equipment manufacturer’s requirements.