Product Specifications

Riser Anchor Clamp.

- General

  - Provide anchors on pipe risers as indicated on contract documents or as required.

  - Anchor attachment shall not require welding.

  - Anchor is supplied in 2 halves and will clamp to a pipe/tubing passing through a floor penetration.

- Products

  - Riser anchor clamp shall be RAC as manufactured by The Metraflex Co.® Chicago, IL.

  - Anchor clamp body shall be Ductile Iron conforming to ASTM A-536.

  - Anchor clamp gripping teeth shall be case hardened carbon steel.

  - Anchor clamp shall be rated for the below loads:

Size	Load

2.5”	9,000 lbs.

3”	10,000 lbs.

4”	20,000 lbs.

5”	25,000 lbs.

6”	30,000 lbs.

8”	50,000 lbs.

  - Required bolt torque should be cast into the housing.

  - Openings to allow for installation and inspection of fire proofing caulk are required.

- Execution

  - Installation shall be in accordance with Manufacturer’s installation instructions.

  - Consult manufactures installation instructions for contact area detail and bolt torque.