Product Specifications

SSFT Y Strainer.

- General:

  - “Y” Pattern strainers with FPT ends shall be installed where shown on plans or required by equipment manufacturers.

  - Strainer shall remove debris from the pipeline to prevent damage to other equipment.  When possible, screen opening size shall be coordinated with the other equipment manufacturers.

- Product:

  - Y Strainer shall be model “SSFT" as manufactured by The Metraflex Company®, Chicago, IL.

  - Materials

    - Strainer body shall be Type 304 Stainless Steel

    - Screens shall be Type 304 Stainless steel.

  - Strainer connection shall be FPT in accordance with ANSI B1.20.1.

  - Pressure rating shall be 200 PSI at 150⁰ F.

  - Screen perforations shall be 20 mesh.

  - Screens shall be removable via an access cover sealed with Teflon gasket.

  - Strainer shell be lead free in accordance with NSF 372.

- Execution:

  - Y Strainer shall be installed in accordance with manufacturer’s recommendations and contact requirements.

  - Screen perforation shall be in accordance with equipment manufacturer’s recommendations.