# Inline Seismic Expansion Joint:

- General:

- Provide Inline seismic expansion joints as indicated on the contract drawings or as required to accommodate any seismic or building movement of the piping system.

- Seismic joints to utilize both externally pressurized bellows and gimbal joints to achieve movement.

- All joints to be provided with drain connection and lifting lug.

- All materials of construction, pressure ratings, and end fittings shall be appropriate for the application. Guiding and anchoring per EJMA recommendations and guidelines

2. Products.

- Manufacturer: Expansion joints shall be “Seismic Gator” as manufactured by The Metraflex Company®, Chicago, IL.

- Seismic joints shall conform to ASTM F-2934.

C.  Performance:  Expansion joints shall be pressure rated for 150 psi @ 500⁰ F

D.	Test pressure for 150 PSI joints shall be 225 PSI at 70⁰ F.

E.	Movement capabilities for single joints shall be +- 4” in X, Y, and Z planes.

F.	End connections shall be fixed carbon steel plate flange one end, floating carbon steel plate flange other end.

3.	Execution

A.	Anchoring: Seismic Gator will develop inline bellows anchor loads that must be properly restrained.  Anchors shall be used in place of first seismic bracing.

B.	Drain:	Expansion joint shall be installed so that the drain connection is on the low end of the joint.

C.	Installation shall be in accordance with manufacturers

Product Specifications

printed instructions.