Product Specifications

Spider Type Pipe Guides.

- General

  - Provide pipe guides as indicated on project plans or in accordance with EJMA guidelines based on design pressure and line size.

  - Primary and intermediate guides shall be spider type.

- Products

  - Pipe guides shall be style “PGIV” as manufactured by The Metraflex Company®, Chicago, IL.

  - All components shall be manufactured in compliance with the Manufacturer's Standardization Society (MSS) SP-58 and SP-89

  - Guide shall be made up of a guide cylinder with bolt down base and a two-section guide spider with 1/8” clearance.

  - Guide shall be made up of ASTM A-134 carbon steel.

  - Guide cylinder shall be sized to accommodate pipe insulation.

  - Guide spider shall be sized to accommodate thermal movement.

  - All surfaces of guide shall have Alkyd corrosion resistant paint.

- Execution

  - Install and guide per manufacturer’s installation instructions and Mechanical Contractors Association of America “Guidelines for Quality Piping Installations”.

  - Spider type guides are rated to restrain lateral loads only and do not replace pipe supports.