Style S 250 lb. FPT Y Strainer

- General:

  - “Y” Pattern strainers with FPT ends shall be installed where shown on plans or required by equipment manufacturers.

  - Strainer shall remove debris from the pipeline to prevent damage to other equipment.  When possible, screen opening size shall be coordinated with the other equipment manufacturers.

- Product:

  - Y Strainer shall be model “Style S" as manufactured by The Metraflex Company®, Chicago, IL.

  - Materials

    - Strainer body shall be ASTM A126 B Cast Iron.

    - Screens shall be Type 304 Stainless steel.

  - End shall be FPT in accordance with ANSI B1.20.1.

  - Screen perforations shall be:

    - For liquid service for sizes .5” – 2” perforation shall be 20 mesh.

    - For liquid service for sizes 2.5” – 3” perforation shall be .063”.

    - For steam service for sizes 5” – 2” perforation shall be 20 mesh.

    - For steam service for sizes 2.5” – 3” perforation shall be .045”.

  - Pressure ratings shall be:

    - For liquid service 400 PSI at 150⁰ F.

    - For steam service 250 lb. at 400⁰ F

  - Screens shall be removable via an access cover.

  - Strainer shell be lead free in accordance with NSF 372.

- Execution:

  - Y Strainer shall be installed in accordance with manufacturer’s recommendations and contact requirements.

  - Pressure drop values shall comply with Fluid Controls Institute Standard for performance testing strainers for liquid service.

  - Screen perforation shall be in accordance with equipment manufacturer’s.