Product Specifications

Flexible Hose Connector with Carbon Steel Flanged Ends and Flow Conditioning Vanes.

- General

  - Provide flexible hose connector(s) as indicated on the contract drawings or as required to accommodate any vibration of thermal expansion and contraction of the piping system.

  - Flexible hose connectors shall be manufactured complete with section of corrugated metal house, and braid, with carbon steel plate flange end connections.

  - Connectors mounted at the suction side of pumps located upstream of the inlet elbow shall incorporate specially designed stationary vanes that impart a rotational motion as the fluid enters the elbow. Vanes to be capable of counteracting elbow induced turbulence, enabling the fluid to negotiate the turn uniformly, and exit with a flat velocity profile.

- Products

  - Flexible hose connectors with flow straightening vanes shall be Suction Diffuser Flex manufactured by The Metraflex Company®, Chicago, IL.

  - Corrugated Hose shall be type 304 Stainless Steel.

  - Braid shall be type 304 Stainless Steel.

  - End fittings shall be carbon steel plate flange with 150 lb. drilling.

- Execution

  - Install per manufacturer’s installation instructions and Mechanical Contractors Association of America “Guidelines for Quality Piping Installations”.