Note to users: items shown in red indicated edits / selections that need to be made to tailor the specification for the application.

Product Specifications

VRF Metraloop.

- General

  - Provide flexible hose expansion loop(s) as indicated on the contract drawings or as required to accommodate any thermal expansion or contraction.

  - Flexible hose expansion loops shall be manufactured complete with two parallel sections of corrugated metal house, compatible braid, 180⁰ return bend, with inlet and outlet connections.  Field fabricated loops shall not be acceptable.

  - Flexible hose expansion loops shall impart no thrust loads to system support, anchors or building structure.

- Products

  - Flexible hose expansion loops to be "VRF Metraloop®” as manufactured by The Metraflex Company®, Chicago, IL.

  - Corrugated Hose shall be Type 321 stainless Steel.

  - Braid shall be double layer of type 304 Stainless Steel.

  - Fittings shall be Sch 40 S Type 304 Stainless in accordance with ASTM A240.

  - Copper pipe systems, the VRF Metraloop shall be equipped with a stainless-steel to copper conversion fitting with XHP copper stub ends.

  - Flexible hose expansion loops shall have a factory supplied; hanger / support lug located at the bottom of the 180⁰ return.

- Execution

  - Install and guide per manufacturers’ installation instructions and Mechanical Contractors Association of America “Guidelines for Quality Piping Installations”.

  - Flexible hose expansion loop return fitting shall be supported to allow movement.